## Tool Guide
Logic Description of Tool
The tool follows the logic below in the calculation of outputs using the inputs provided:
Check the Average heat required (kW) field against the refrigerant size range. Return no output if outside available machine range
Check the Annual Process Heating Cost ($ p.a.) or Process Hours of Use p.a. inputs against Average heat required (kW) to ensure data is possible (i.e. utilisation of the heating system is less than 100%). Return no output if inputs are impossible.
Check whether cooling is usable from Heat source and Is cooling usable?. For cooling applications, the capex cost is increased by 20%.
Search for the correct capital expenditure based on Average heat required (kW)
Search for the correct heat source in temperature based on Heat source, Location, and Heat source in temperature (C). This is rounded to the nearest multiple of 5
Round the Heat sink out temperature (C) to the nearest multiple of 5
Search for and provide the COP (heating) and COP (cooling) based on backend data tables.
Provide Capex and Opex (Maintenance and Energy) figures based on backend data tables and Current electricity cost ($/kWh). If data is entered into the Portion of energy use of heat pumps from solar (%) field, the electricity cost is a weighted average of the entered electricity cost and $0.06/kWh at the entered solar percentage. This is the estimated Levelised Cost of Energy (LCOE) of the solar system.
Calculate the current heating energy cost (not shown in outputs) by incorporating the Current heating system efficiency. The efficiency defaults to 0.8 if no value is entered.
Incorporate the Other operating costs of current system ($ p.a.) to calculate Net Savings and Simple Payback (years), with error displays to show “No Payback” if Net Savings is less than $0.
Calculate the Current LCOE of heating energy delivered ($/kWh) using Capital cost of current heating system ($) and Current system rated life (yr).
Calculate the Heat pump LCOE of heating energy delivered using the Capex and Opex (Maintenance and Energy). Heat pump is assumed to have a life of 25 years.
Calculated the Storage size (kWh) and Capex of Thermal Storage using Peak heating requirement (kW) and Maximum hours of continuous peak heating use inputs.
Calculate the NPV over 10 years by incorporating thermal storage.
To update the data tables used by this tool, simply adjust the relevant refrigerant tab. For adjustments that increase the size of the data tables, the relevant formulaic changes much be made in the Selection Tool tab so that the new data is referenced. The Trace Dependents function will point out all the relevant array updates required.

## Selection Tool
Manual Inputs (Basic)
| Current heating fuel cost ($/GJ) | 15 |  |  | Image source: |  | http://www.veoliawater2energy.com/en/references/heat-pumps/
OR | Annual Process Heating Cost ($ p.a.) | 50000 |  |  |  | Average heat required (kW) | 500
OR | Process Hours of Use p.a. |  |  |  |  | Peak heating requirement (kW) - if known | 600
| Current electricity cost ($/kWh) | 0.1 |  |  |  | Maximum hours of continuous peak heating use (hrs) | 1
| Heat source | Water
| Location | Brisbane |  | Heat source in temperature (C) | 25 |  |  |  | 75 | Heat sink out temperature (C)
| Is Load Flex/Demand Response Required (min 1MWe load) | Yes
| Duration of Load Flex Desired (minutes) | 30
| Manual Inputs (Advanced) | [10 empty] | Average heat sink return flow rate (L/s, water only)
Heat source air temperature (C)
Current heating system efficiency (%)
Other operating costs of current system ($ p.a.)
Capital cost of current heating system ($)
Current system rated life (yr)
Discount rate for NPV calculation (%)
Portion of energy use of heat pumps from solar (%)
|  |  |  | Heat source out temperature (C) | 20 |  |  |  | 35 | Average heat sink return/in temperature (C, water only)
|  |  |  | Is cooling usable? | YES
Outputs
|  | Ammonia (R717) | CO2 (R744) |  |  |  | Thermal Battery Dimensions (Approximate)
| Annual heating energy use (MJ) | 2333000 | 2333000 |  |  |  | Above ground tank - preferred if stratified heat is desired | [6 empty] | Below ground tanks - lower capital and maintenance costs at the expense of performance. Not suitable for small systems
| Max heat pump electrical demand (kVA) | 142.2464 | 121.7636 | [5 empty] | D = | 2 | m
| Heat pump size required (kW thermal) | 500 | 500
| COP (heating) | 3.7 | 4.3224
| COP (cooling) | 3 | 1 | [11 empty] | D = | 3 | m | Header tank (size not included in thermal battery)
| Maximum cooling power (kW) | 405.4023 | 115.6755
| Capex | 576000 | 570000
| Opex (Maintenance and Energy) | 14000 | 17900 |  |  | H = | 3.8197 | m |  |  |  |  | H = | 1.6977 | m
| Storage size (kWh) | 525 | 525
| Capex of Thermal Storage | 64851.8115 | 64851.8115
| Net Savings | 36000 | 32000
| Additional Revenue from Load Flex/Demand Response | 0 | 0
| Simple Payback (years) | 17.8014 | 19.8391
Adv. | Current LCOE of heating energy delivered ($/kWh) | #DIV/0! | #DIV/0!
Adv. | Heat pump LCOE of heating energy delivered ($/kWh)) | 0.031564 | 0.051004
Adv. | Required storage recharge time (hr/day) | 1.05 | 1.05
Adv. | NPV over 10 years | -280851.8115 | -314851.8115
Checks and Data (HIDE)
|  | R717 | R744
| Sizing check 1 (equipment) | 1 | 1
| Sizing check 2 (utilisation) | 1 | 1
| Cooling Check | 1.2 | 1.2
| Capex Check | 960 | 950
| Heat source in temperature | 25 | 25
| Heat sink out temperature | 75 | 75
| Heat source out temperature | 20 | 20
| Heat sink in temperature | 35 | 35
| Current system efficiency | 0.7 | 0.7
| PV Cost of electricity ($/kWh) | 0.06 | 0.06
| Utilisation rate check | 1 | 1
| Thermal storage size needed (kWh, with 50% extra) | 525 | 525
| Heating utilization | 14.8% | 14.8%
| Thermal storage volume (L) | 12000 | 12000
| Load Flex + DR + FCAS + RERT Revenue Stream Factor ($/MW/year) | 40000 | 40000
| Assumed Annual DR requirement (hours) | 3 | 3

## Refrigerant Guide
105
100
95
90
85
80
75
70
65
60
55
50
| 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 900 | 1000
Ammonia
Lower efficiency at higher temperatures
Uneconomical at lower capacities
Capacity up to 40MW and higher
CO2
Better performance above ~85C
Available & economical at low capacities
Refrigerant Comparison CO2 vs Ammonia
Heat pump capacity in kWth
Heat sink out temp 0C

## R717
| Min | Max
Heating Capacity Range (kW) | 100 | 20000
Heat Sink Out Temperature Range (C) |  | 85
Heat Source In Temperature Range (C)
| 0 | 250 | 750 | 1750
Cost of heat pump ($/kW heat) | 1100 | 960 | 560 | 320
Maintenance costs (% of capex) | 0.0075
COP Tables
Heating (water to water) | Heat Sink Out Temperature
Heat Source In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85
0 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725 | 2.4494 | 2.3391
5 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725 | 2.4494
10 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725
15 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711
20 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681
25 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048
30 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501 | 3.2563
35 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928 | 3.501
40 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148 | 3.7928
45 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911 | 4.148
50 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617 | 4.5911
55 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289 | 5.1617
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2 | 5.9289
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2 | 6.2
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2 | 6.2
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 6.2
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cooling (water to water) | Heat Source Out Temperature
Heat Source In Temperature | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45
0 | 1.8 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 1.8 | 1.9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1.8 | 1.9 | 2 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0
25 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 0 | 0 | 0 | 0 | 0
30 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 0 | 0 | 0 | 0
35 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 0 | 0 | 0
40 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 0 | 0
45 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 0
50 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
55 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
60 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
65 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
70 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
75 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
80 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
85 | 1.8 | 1.9 | 2 | 2.1 | 2.3 | 2.8 | 3 | 2.8 | 2.5 | 2.3 | 2.2 | 2.2
Heating (air to water) | Heat Source Out Temperature -10: Heat Sink Out Temperature
Heat Source In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85
0 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725 | 2.4494 | 2.3391
5 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725 | 2.4494
10 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711 | 2.5725
15 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681 | 2.711
20 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048 | 2.8681
25 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563 | 3.048
30 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501 | 3.2563
35 | 0 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928 | 3.501
40 | 0 | 0 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148 | 3.7928
45 | 0 | 0 | 0 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.148
50 | 0 | 0 | 0 | 0 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
55 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
COP adjustments for Heat Sink In Temperatures | Heat Source Out Temperature -10: Heat Sink Out Temperature
Heat Sink In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85
5
10
15 | Heat Source Out Temperature 20: 0.30111; Heat Source Out Temperature 25: 0.28928; Heat Source Out Temperature 30: 0.33636; Heat Source Out Temperature 35: 0.34417
20 | Heat Source Out Temperature 20: 0.26574; Heat Source Out Temperature 25: 0.26693; Heat Source Out Temperature 30: 0.32068; Heat Source Out Temperature 35: 0.3289; Heat Source Out Temperature 40: 0.38167
25 | Heat Source Out Temperature 20: 0.22323; Heat Source Out Temperature 25: 0.24082; Heat Source Out Temperature 30: 0.29008; Heat Source Out Temperature 35: 0.30727; Heat Source Out Temperature 40: 0.35947
30 | Heat Source Out Temperature 20: 0.18192; Heat Source Out Temperature 25: 0.20066; Heat Source Out Temperature 30: 0.256; Heat Source Out Temperature 35: 0.27906; Heat Source Out Temperature 40: 0.33265
35 | Heat Source Out Temperature 20: 0.081921; Heat Source Out Temperature 25: 0.11266; Heat Source Out Temperature 30: 0.1735; Heat Source Out Temperature 35: 0.19906; Heat Source Out Temperature 40: 0.25598
40 | Heat Source Out Temperature 20: -0.022079; Heat Source Out Temperature 25: 0.016656; Heat Source Out Temperature 30: 0.081001; Heat Source Out Temperature 35: 0.11656; Heat Source Out Temperature 40: 0.17598
45 | Heat Source Out Temperature 20: -0.12608; Heat Source Out Temperature 25: -0.073344; Heat Source Out Temperature 30: -0.0064994; Heat Source Out Temperature 35: 0.036562; Heat Source Out Temperature 40: 0.092646
50 | Heat Source Out Temperature 20: -0.23408; Heat Source Out Temperature 25: -0.16734; Heat Source Out Temperature 30: -0.098999; Heat Source Out Temperature 35: -0.045938; Heat Source Out Temperature 40: 0.012646
55 | Heat Source Out Temperature 20: -0.34008; Heat Source Out Temperature 25: -0.26134; Heat Source Out Temperature 30: -0.1915; Heat Source Out Temperature 35: -0.13094; Heat Source Out Temperature 40: -0.070687
60 | Heat Source Out Temperature 25: -0.36134; Heat Source Out Temperature 30: -0.289; Heat Source Out Temperature 35: -0.22094; Heat Source Out Temperature 40: -0.15735
65 | Heat Source Out Temperature 30: -0.3865; Heat Source Out Temperature 35: -0.31094; Heat Source Out Temperature 40: -0.24735
70 | Heat Source Out Temperature 35: -0.40344; Heat Source Out Temperature 40: -0.33735
75 | Heat Source Out Temperature 40: -0.42402
[13 empty] | Mayakawa COP data for 80C sink out | [14 empty] | Change in COP from Average
[13 empty] | source in\sink in | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | Avg | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75
[13 empty] | 30 |  | 4.1 | 4.03 | 3.96 | 3.9 | 3.83 | 3.76 | 3.69 | 3.62 | 3.55 | 3.47 | 3.39 | 3.32 | 3.7183 |  | 0.38167 | 0.31167 | 0.24167 | 0.18167 | 0.11167 | 0.041667 | -0.028333 | -0.098333 | -0.16833 | -0.24833 | -0.32833 | -0.39833
[13 empty] | 35 |  |  | 4.57 | 4.49 | 4.41 | 4.33 | 4.25 | 4.17 | 4.09 | 4 | 3.91 | 3.83 | 3.74 | 4.1627 |  |  | 0.40727 | 0.32727 | 0.24727 | 0.16727 | 0.087273 | 0.0072727 | -0.072727 | -0.16273 | -0.25273 | -0.33273 | -0.42273
[13 empty] | 40 |  |  |  | 5.11 | 5.02 | 4.93 | 4.83 | 4.74 | 4.64 | 4.54 | 4.44 | 4.33 | 4.23 | 4.681 |  |  |  | 0.429 | 0.339 | 0.249 | 0.149 | 0.059 | -0.041 | -0.141 | -0.241 | -0.351 | -0.451
[29 empty] | 0.38167 | 0.35947 | 0.33265 | 0.25598 | 0.17598 | 0.092646 | 0.012646 | -0.070687 | -0.15735 | -0.24735 | -0.33735 | -0.42402
[13 empty] | Mayakawa data for 75C sink out | [14 empty] | Change in COP from Average
[13 empty] | source in\sink in | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 |  | Avg | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70
[13 empty] | 25 | 3.88 | 3.82 | 3.76 | 3.7 | 3.64 | 3.57 | 3.51 | 3.45 | 3.38 | 3.31 | 3.24 | 3.17 |  | 3.5358 | 0.34417 | 0.28417 | 0.22417 | 0.16417 | 0.10417 | 0.034167 | -0.025833 | -0.085833 | -0.15583 | -0.22583 | -0.29583 | -0.36583
[13 empty] | 30 |  | 4.39 | 4.32 | 4.24 | 4.17 | 4.1 | 4.02 | 3.95 | 3.87 | 3.79 | 3.71 | 3.62 |  | 4.0164 |  | 0.37364 | 0.30364 | 0.22364 | 0.15364 | 0.083636 | 0.0036364 | -0.066364 | -0.14636 | -0.22636 | -0.30636 | -0.39636
[13 empty] | 35 |  |  | 4.91 | 4.83 | 4.74 | 4.65 | 4.57 | 4.48 | 4.39 | 4.29 | 4.2 | 4.1 |  | 4.516 |  |  | 0.394 | 0.314 | 0.224 | 0.134 | 0.054 | -0.036 | -0.126 | -0.226 | -0.316 | -0.416
[13 empty] | 40 |  |  |  | 5.52 | 5.42 | 5.32 | 5.22 | 5.11 | 5.01 | 4.9 | 4.78 | 4.67 |  | 5.1056 |  |  |  | 0.41444 | 0.31444 | 0.21444 | 0.11444 | 0.0044444 | -0.095556 | -0.20556 | -0.32556 | -0.43556
[13 empty] | Mayakawa data for 70C sink out | [14 empty] | 0.34417 | 0.3289 | 0.30727 | 0.27906 | 0.19906 | 0.11656 | 0.036562 | -0.045938 | -0.13094 | -0.22094 | -0.31094 | -0.40344
Change in COP from Average
[13 empty] | source in\sink in | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 |  |  | Avg | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65
[13 empty] | 25 | 4.16 | 4.1 | 4.03 | 3.96 | 3.9 | 3.83 | 3.76 | 3.69 | 3.62 | 3.54 | 3.47 |  |  | 3.8236 | 0.33636 | 0.27636 | 0.20636 | 0.13636 | 0.076364 | 0.0063636 | -0.063636 | -0.13364 | -0.20364 | -0.28364 | -0.35364
[13 empty] | 25 |  | 4.72 | 4.64 | 4.56 | 4.48 | 4.4 | 4.32 | 4.24 | 4.15 | 4.06 | 3.98 |  |  | 4.355 |  | 0.365 | 0.285 | 0.205 | 0.125 | 0.045 | -0.035 | -0.115 | -0.205 | -0.295 | -0.375
[13 empty] | 25 |  |  | 5.3 | 5.21 | 5.12 | 5.02 | 4.93 | 4.83 | 4.73 | 4.63 | 4.52 |  |  | 4.9211 |  |  | 0.37889 | 0.28889 | 0.19889 | 0.098889 | 0.0088889 | -0.091111 | -0.19111 | -0.29111 | -0.40111
[13 empty] | 25 |  |  |  | 6 | 5.9 | 5.78 | 5.67 | 5.55 | 5.44 | 5.32 | 5.19 |  |  | 5.6063 |  |  |  | 0.39375 | 0.29375 | 0.17375 | 0.06375 | -0.05625 | -0.16625 | -0.28625 | -0.41625
25
[13 empty] | 25 | [14 empty] | 0.33636 | 0.32068 | 0.29008 | 0.256 | 0.1735 | 0.081001 | -0.0064994 | -0.098999 | -0.1915 | -0.289 | -0.3865
[13 empty] | Mayakawa data for 65C sink out | [14 empty] | Change in COP from Average
[13 empty] | source in\sink in | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 |  |  |  | Avg | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
[13 empty] | 20 | 3.87 | 3.81 | 3.75 | 3.69 | 3.63 | 3.56 | 3.5 | 3.44 | 3.37 | 3.3 |  |  |  | 3.6244 | 0.24556 | 0.18556 | 0.12556 | 0.065556 | 0.0055556 | -0.064444 | -0.12444 | -0.18444 | -0.25444 | -0.32444
[13 empty] | 25 | 4.48 | 4.41 | 4.34 | 4.26 | 4.19 | 4.11 | 4.04 | 3.96 | 3.88 | 3.8 |  |  |  | 4.147 | 0.333 | 0.263 | 0.193 | 0.113 | 0.043 | -0.037 | -0.107 | -0.187 | -0.267 | -0.347
[13 empty] | 30 |  | 5.1 | 5.02 | 4.93 | 4.84 | 4.75 | 4.66 | 4.57 | 4.48 | 4.38 |  |  |  | 4.7478 |  | 0.35222 | 0.27222 | 0.18222 | 0.092222 | 0.0022222 | -0.087778 | -0.17778 | -0.26778 | -0.36778
[13 empty] | 35 |  |  | 5.77 | 5.66 | 5.56 | 5.45 | 5.35 | 5.24 | 5.13 | 5.02 |  |  |  | 5.3975 |  |  | 0.3725 | 0.2625 | 0.1625 | 0.0525 | -0.0475 | -0.1575 | -0.2675 | -0.3775
[13 empty] | 40 |  |  |  | 6.58 | 6.46 | 6.33 | 6.2 | 6.07 | 5.95 | 5.81 |  |  |  | 6.2 |  |  |  | 0.38 | 0.26 | 0.13 | 0 | -0.13 | -0.25 | -0.39
45
[13 empty] | 50 | [14 empty] | 0.28928 | 0.26693 | 0.24082 | 0.20066 | 0.11266 | 0.016656 | -0.073344 | -0.16734 | -0.26134 | -0.36134
[13 empty] | Mayakawa data for 60C sink out | [14 empty] | Change in COP from Average
[13 empty] | source in\sink in | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 |  |  |  |  | Avg | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55
[13 empty] | 20 | 4.18 | 4.11 | 4.04 | 3.98 | 3.91 | 3.84 | 3.77 | 3.69 | 3.62 |  |  |  |  | 3.9044 | 0.27556 | 0.20556 | 0.13556 | 0.075556 | 0.0055556 | -0.064444 | -0.13444 | -0.21444 | -0.28444
[13 empty] | 25 | 4.85 | 4.77 | 4.69 | 4.61 | 4.53 | 4.44 | 4.36 | 4.27 | 4.19 |  |  |  |  | 4.5233 | 0.32667 | 0.24667 | 0.16667 | 0.086667 | 0.0066667 | -0.083333 | -0.16333 | -0.25333 | -0.33333
[13 empty] | 30 |  | 5.55 | 5.45 | 5.36 | 5.26 | 5.16 | 5.06 | 4.95 | 4.85 |  |  |  |  | 5.205 |  | 0.345 | 0.245 | 0.155 | 0.055 | -0.045 | -0.145 | -0.255 | -0.355
[13 empty] | 35 |  |  | 6.31 | 6.2 | 6.09 | 5.97 | 5.85 | 5.73 | 5.6 |  |  |  |  | 5.9643 |  |  | 0.34571 | 0.23571 | 0.12571 | 0.0057143 | -0.11429 | -0.23429 | -0.36429
[13 empty] | 40 |  |  |  | 7.27 | 7.13 | 6.99 | 6.84 | 6.7 | 6.55 |  |  |  |  | 6.9133 |  |  |  | 0.35667 | 0.21667 | 0.076667 | -0.073333 | -0.21333 | -0.36333
45
[13 empty] | 50 | [14 empty] | 0.30111 | 0.26574 | 0.22323 | 0.18192 | 0.081921 | -0.022079 | -0.12608 | -0.23408 | -0.34008
55
60

## R744
| Min | Max
Heating Capacity Range (kW) | 50 | 5000
Heat Sink Out Temperature Max (°C) |  | 65 to 90
Heat source in temperature range (°C) |  | -5 to 37
| 0 | 250 | 750 | 1750
Cost of heat pump ($/kW heat) | 1400 | 950 | 650 | 500
Maintenance costs (% of capex) | 0.01
COP Tables
Heating (water to water) | Heat Sink Out Temperature
Heat Source In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85
0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3.4 | 3.4 | 3.4
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3.9 | 4.5 | 3.4 | 3.4 | 3.4
10 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4.8 | 4.5 | 4.1 | 3.8
15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4.8 | 4.8 | 4.5 | 4.1
20 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1027 | 4.7 | 4.8 | 4.8 | 4.5
25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.1 | 4.7 | 4.7 | 4.8 | 4.8
30 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 4.6 | 4.7 | 4.7 | 4.8
35 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3.9 | 4 | 4.6 | 4.7 | 4.7
40 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 3.9 | 4 | 4 | 4.6 | 4.7
45 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 4 | 4 | 4 | 4.6
50 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 3 | 3.5 | 4 | 4 | 4
55 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 3.5 | 3.5 | 4 | 4
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3.5 | 3.5 | 4
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3.5 | 4
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | 3
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3
Cooling (water to water) | Heat Source Out Temperature
Heat Source In Temperature | -10 | -5 | 0 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45
0 | 2.8 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 2.8 | 2.7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 2.8 | 2.7 | 2.7 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0
25 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 0 | 0 | 0 | 0 | 0
30 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 0 | 0 | 0 | 0
35 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 0 | 0 | 0
40 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 0 | 0
45 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 0
50 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
55 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
60 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
65 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
70 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
75 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
80 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
85 | 2.8 | 2.7 | 2.7 | 2.6 | 2 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1
Heating (air to water) | Heat Source Out Temperature -10: Heat Sink Out Temperature | Linear regression
Heat Source In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | m | b
0 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 2.3983 | 2.2804 | 2.1625 | 2.0446 | 1.9267 | -0.023583 | 3.9312 |  | Recent Advances in Transcritical CO2 (R744) Heat Pump System: A Review
5 | 1 | 1 | 2.1 | 2 | 1.5 | 1.5 | 3.5 | 2.71 | 2.5931 | 2.4761 | 2.3592 | 2.2422 | -0.023389 | 4.2303
10 | 1 | 1 | 2.1 | 2 | 1.5 | 1.5 | 4.2 | 3.5317 | 3.3176 | 3.1036 | 2.8896 | 2.6756 | -0.042806 | 6.314 |  | https://www.automaticheating.com.au/solutions/co2-heat-pump-hot-water-heating-solutions/
15 | 1 | 1 | 3 | 2.5 | 2 | 1.5 | 4.3 | 4.0667 | 3.7739 | 3.4811 | 3.1883 | 2.8956 | -0.058556 | 7.8728
20 | 1 | 1 | 3 | 2.5 | 2 | 1.5 | 4.9 | 4.4067 | 4.0728 | 3.7389 | 3.405 | 3.0711 | -0.066778 | 8.7472 |  | http://www.r744.com/files/pdf_672.pdf
25 | 1 | 1 | 3.3 | 2.7 | 2.1 | 1.5 | 4.9 | 4.73 | 4.3564 | 3.9828 | 3.6092 | 3.2356 | -0.074722 | 9.5869
30 | 0 | 1 | 3.3 | 2.7 | 2.1 | 1.5 | 4.7 | 4.865 | 4.474 | 4.0831 | 3.6921 | 3.3011 | -0.078194 | 9.9476 |  | https://www.laros.com.au/wp-content/uploads/2016/03/LAROS-SANDEN-Laboratory-Assessment-Sanden-Heat-Pump.pdf
35 | 0 | 0 | 3.3 | 2.7 | 2.1 | 1.5 | 4.3 | 4.99 | 4.5844 | 4.1789 | 3.7733 | 3.3678 | -0.081111 | 10.2622
40 | 0 | 0 | 0 | 1 | 1 | 1 | 4.1 | 5.1233 | 4.7147 | 4.3061 | 3.8975 | 3.4889 | -0.081722 | 10.4353 |  | https://www.sandenwaterheater.com/sanden/assets/File/Sanden_sanc02_technical-info_10-2017_4.pdf
45 | 0 | 0 | 0 | 0 | 1 | 1 | 3.7 | 4 | 4 | 3.6 | 3.6 | 3.4889
50 | 0 | 0 | 0 | 0 | 0 | 1 | 3.7 | 4 | 4 | 3.6 | 3.6 | 3.4889
55 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7 | 4 | 4 | 3.6 | 3.6 | 3.4889
COP adjustments for Heat Sink In Temperatures | Heat Source Out Temperature -10: Heat Sink Out Temperature | Linear regression
Heat Sink In Temperature | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | m | b
5 | Heat Source Out Temperature 20: 0.28378; Heat Source Out Temperature 25: 0.35648; Heat Source Out Temperature 30: 0.42918; Heat Source Out Temperature 35: 0.50188; Heat Source Out Temperature 40: 0.57458; Heat Source Out Temperature 45: 0.64728 | 0.01454 | -0.58863
10 | Heat Source Out Temperature 20: 0.12489; Heat Source Out Temperature 25: 0.20981; Heat Source Out Temperature 30: 0.29474; Heat Source Out Temperature 35: 0.37966; Heat Source Out Temperature 40: 0.46458; Heat Source Out Temperature 45: 0.54951 | 0.016985 | -0.89418
15 | Heat Source Out Temperature 20: -0.016775; Heat Source Out Temperature 25: 0.037593; Heat Source Out Temperature 30: 0.09196; Heat Source Out Temperature 35: 0.14633; Heat Source Out Temperature 40: 0.20069; Heat Source Out Temperature 45: 0.25506 | 0.010873 | -0.66918
20 | Heat Source Out Temperature 20: -0.20427; Heat Source Out Temperature 25: -0.11241; Heat Source Out Temperature 30: -0.02054; Heat Source Out Temperature 35: 0.071327; Heat Source Out Temperature 40: 0.16319; Heat Source Out Temperature 45: 0.25506 | 0.018373 | -1.3067
25 | Heat Source Out Temperature 20: -0.41677; Heat Source Out Temperature 25: -0.28241; Heat Source Out Temperature 30: -0.14804; Heat Source Out Temperature 35: -0.013673; Heat Source Out Temperature 40: 0.12069; Heat Source Out Temperature 45: 0.25506 | 0.026873 | -2.0292
30 | Heat Source Out Temperature -10: N/A; Heat Source Out Temperature 20: -0.7565; Heat Source Out Temperature 25: -0.58019; Heat Source Out Temperature 30: -0.40387; Heat Source Out Temperature 35: -0.22756; Heat Source Out Temperature 40: -0.05125; Heat Source Out Temperature 45: 0.12506 | 0.035262 | -2.8722
35 | N/A | N/A |  |  |  |  | -0.9065 | -0.73019 | -0.55387 | -0.37756 | -0.20125 | -0.024938 | 0.035262 | -3.0222
40 | N/A | N/A | N/A |  |  |  | -1.0407 | -0.88019 | -0.71971 | -0.55923 | -0.39875 | -0.23827 | 0.032096 | -2.9664
45 | N/A | N/A | N/A | N/A |  |  | -1.1782 | -1.0302 | -0.88221 | -0.73423 | -0.58625 | -0.43827 | 0.029596 | -2.9539
50 | N/A | N/A | N/A | N/A | N/A |  | -1.3157 | -1.1802 | -1.0447 | -0.90923 | -0.77375 | -0.63827 | 0.027096 | -2.9414
55 | N/A | N/A | N/A | N/A | N/A | N/A | -1.4532 | -1.3302 | -1.2072 | -1.0842 | -0.96125 | -0.83827 | 0.024596 | -2.9289
60 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -1.4802 | -1.3733 | -1.2665 | -1.1596 | -1.0527 | 0.021373 | -2.8695
65 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -1.5233 | -1.4165 | -1.3096 | -1.2883
[14 empty] | Mayakawa COP data for 90C sink out | [10 empty] | Change in COP from Average
[14 empty] | source in\sink in | 5 | 9 | 10 | 17 | 24 | 29 | 40 | 60 | 65 | Avg | 5 | 9 | 10 | 17 | 24 | 29 | 40 | 60 | 65
[14 empty] | 0 | 2.32 | 2.26 | 2.23 | 2.18 | 2.1 | 2.05 | 1.85 | 1.27 | 1.08 | 1.9267 | 0.39333 | 0.33333 | 0.30333 | 0.25333 | 0.17333 | 0.12333 | -0.076667 | -0.65667 | -0.84667
[14 empty] | 5 | 2.71 | 2.67 | 2.65 | 2.56 | 2.44 | 2.32 | 2.12 | 1.45 | 1.26 | 2.2422 | 0.46778 | 0.42778 | 0.40778 | 0.31778 | 0.19778 | 0.077778 | -0.12222 | -0.79222 | -0.98222
[14 empty] | 10 | 3.32 | 3.24 | 3.22 | 3.04 | 2.85 | 2.71 | 2.39 | 1.74 | 1.57 | 2.6756 | 0.64444 | 0.56444 | 0.54444 | 0.36444 | 0.17444 | 0.034444 | -0.28556 | -0.93556 | -1.1056
[14 empty] | 15 | 3.59 | 3.51 | 3.47 | 3.35 | 3.14 | 2.99 | 2.62 | 1.78 | 1.61 | 2.8956 | 0.69444 | 0.61444 | 0.57444 | 0.45444 | 0.24444 | 0.094444 | -0.27556 | -1.1156 | -1.2856
[14 empty] | 20 | 3.82 | 3.73 | 3.68 | 3.54 | 3.32 | 3.18 | 2.75 | 1.91 | 1.71 | 3.0711 | 0.74889 | 0.65889 | 0.60889 | 0.46889 | 0.24889 | 0.10889 | -0.32111 | -1.1611 | -1.3611
[14 empty] | 25 | 4.03 | 3.93 | 3.89 | 3.72 | 3.53 | 3.39 | 2.88 | 2.02 | 1.73 | 3.2356 | 0.79444 | 0.69444 | 0.65444 | 0.48444 | 0.29444 | 0.15444 | -0.35556 | -1.2156 | -1.5056
[14 empty] | 30 | 4.02 | 3.96 | 3.93 | 3.79 | 3.61 | 3.47 | 3.03 | 2.1 | 1.8 | 3.3011 | 0.71889 | 0.65889 | 0.62889 | 0.48889 | 0.30889 | 0.16889 | -0.27111 | -1.2011 | -1.5011
[14 empty] | 35 | 4.02 | 3.98 | 3.96 | 3.85 | 3.7 | 3.56 | 3.17 | 2.19 | 1.88 | 3.3678 | 0.65222 | 0.61222 | 0.59222 | 0.48222 | 0.33222 | 0.19222 | -0.19778 | -1.1778 | -1.4878
[14 empty] | 40 | 4.2 | 4.14 | 4.12 | 3.98 | 3.81 | 3.66 | 3.25 | 2.27 | 1.97 | 3.4889 | 0.71111 | 0.65111 | 0.63111 | 0.49111 | 0.32111 | 0.17111 | -0.23889 | -1.2189 | -1.5189
[25 empty] | 0.64728 |  | 0.54951 | 0.42284 | 0.25506 | 0.12506 | -0.23827 | -1.0527 | -1.2883
[14 empty] | Mayakawa data for 65C sink out | [10 empty] | Change in COP from Average
[14 empty] | source in\sink in | 5 | 9 | 10 | 17 | 24 | 29 |  |  |  | Avg | 5 | 9 | 10 | 17 | 24 | 29
[14 empty] | 0 | 2.59 | 2.48 | 2.42 | 2.38 | 2.29 | 2.23 |  |  |  | 2.3983 | 0.19167 | 0.081667 | 0.021667 | -0.018333 | -0.10833 | -0.16833
[14 empty] | 5 | 2.87 | 2.8 | 2.79 | 2.68 | 2.59 | 2.53 |  |  |  | 2.71 | 0.16 | 0.09 | 0.08 | -0.03 | -0.12 | -0.18
[14 empty] | 10 | 3.8 | 3.76 | 3.74 | 3.57 | 3.29 | 3.03 |  |  |  | 3.5317 | 0.26833 | 0.22833 | 0.20833 | 0.038333 | -0.24167 | -0.50167
[14 empty] | 15 | 4.44 | 4.35 | 4.32 | 4.1 | 3.71 | 3.48 |  |  |  | 4.0667 | 0.37333 | 0.28333 | 0.25333 | 0.033333 | -0.35667 | -0.58667
[14 empty] | 20 | 4.82 | 4.71 | 4.66 | 4.44 | 4.04 | 3.77 |  |  |  | 4.4067 | 0.41333 | 0.30333 | 0.25333 | 0.033333 | -0.36667 | -0.63667
[14 empty] | 25 | 5.15 | 5.03 | 4.97 | 4.74 | 4.43 | 4.06 |  |  |  | 4.73 | 0.42 | 0.3 | 0.24 | 0.01 | -0.3 | -0.67
[14 empty] | 30 | 5.32 | 5.2 | 5.12 | 4.91 | 4.53 | 4.11 |  |  |  | 4.865 | 0.455 | 0.335 | 0.255 | 0.045 | -0.335 | -0.755
[14 empty] | 35 | 5.48 | 5.35 | 5.26 | 5.06 | 4.63 | 4.16 |  |  |  | 4.99 | 0.49 | 0.36 | 0.27 | 0.07 | -0.36 | -0.83
[14 empty] | 40 | 5.56 | 5.47 | 5.43 | 5.28 | 4.77 | 4.23 |  |  |  | 5.1233 | 0.43667 | 0.34667 | 0.30667 | 0.15667 | -0.35333 | -0.89333
[25 empty] | 0.35648 |  | 0.20981 | 0.037593 | -0.28241 | -0.58019

## Validation Data
| Mean max temp (C) | Ground water temperature | Lowest temp | Highest temp | Data Validation | YES
Adelaide | 22.5 | 17 |  |  | Air | NO
Brisbane | 25.5 | 22 |  |  | Ground Water
Canberra | 20 | 17 |  |  | Water
Darwin | 32.1 | 31
Hobart | 17.6 | 14
Melbourne | 19.9 | 17
Perth | 24.8 | 17
Sydney | 21.8 | 17 | 2.1 | 45.8
Load Flex
Yes
No
30
60
90
120
150
180

## Thermal storage
Volume (m3) | Sensible Heat Storage (Euro/kWh) |  | Thermal capacity (kwh/m3) | Phase Change Storage (Euro/kWh) |  |  | Source
300 | 8.18 |  | 110.16 | 13.62 |  |  | https://www.diva-portal.org/smash/get/diva2:956741/FULLTEXT01.pdf
600 | 7.83 |  | 110.41 | 13.59
1000 | 6.97 |  | 66 | 16.96
700 | 4.22 |  | 87.7 | 14.33
2700 | 4.13 |  | 130.88 | 18.83
4500 | 3.7 |  | 138.96 | 19.29
5230 | 2.07 |  | 66.3 | 21.15
5000 | 1.55 |  | 61.8 | 23.79
4500 | 0.86 |  | 61.1 | 23.98
10000 | 1.38 |  | 103.85 | 42.19
10200 | 2.07 |  | 56 | 49.08
10700 | 1.21 |  | 91.95 | 60.95
75000 | 0.71 |  | 126.4 | 68.59
|  |  | 150.1 | 81.22
AVERAGE (with contingency of 1.5) | 5.6618 |  | 192.62 | 84.59
|  |  | 106.95 | 126.52
|  |  | 96.95 | 141.56
|  |  | 70 | 152.06
|  |  | 52.65 | 174.82
|  |  | 132.56 | 359.31
|  |  | AVERAGE (with contingency of 1.5) | 123.5273 | AUD
Thermal Storage Tank Approximate Size
Above-ground Tank |  |  |  |  | Below-ground Tank
Volume (L) | D (m) |  |  |  | Volume | D
0 | N/A |  |  |  | 0 | N/A
1 | 2 |  |  |  | 1 | 3
5000 | 2 |  |  |  | 100000 | 3
10000 | 2 |  |  |  | 200000 | 3
20000 | 4 |  |  |  | 500000 | 7
50000 | 4 |  |  |  | 1000000 | 13
100000 | 6
200000 | 6
300000 | N/A
Material Selection Matrix
Material | Volume | Capital Cost | Maintenance Cost | Performance
Insulated Plastic | <50000 | Low | Medium | High
Insulated Concrete | 10000 - 1000000 | Medium | Low | Medium
Insulated Steel | 0 - 1000000 | High | Low | High